## Instructions
Liquid Typical Speeds
Version 1.1
by Daniel de la Torre
Process Engineer
Intro |  | This template contains a series of calculation sheets to assist you in selecting the pipe dimension for a given flowrate
The main objective is to provide a reference about the proper/economical size of a pipe just having a qucik look at the table
Setup | 1 | There are 2 worksheets, one with Metric units (SI) and one with Imperial units
| 2 | Individual worksheets are protected against inadvertant data entry. Unlocked cells appears with blue text color. No password needed to unlock.
| 3 | To change any other cells, unlock the workbook (from the Tools/Protection pull-down menu)
Data Entry | 4 | Input data appears with blue text color
Results | 5 | Results appear in black text with yellow backgound
Revisions | 6 | Version 1.0 | First version
|  | Version 1.1 | Small corrections before first distribution
Calculations | 7 | Calculations are based on following assumptions
|  | Below 75 mm. |  | 0.9-2-0 m/s
|  | From 75 to 150 mm. |  | 1.5-3.5 m/s
|  | From 100 to 200 mm. |  | 1.8-4.0 m/s
|  | Above 200 mm. |  | 2.4-4.5 m/s
These figures are for guidance only. However, keeping appoximately to these values should provide an economic pipe design
These figures are for water pipes and liquids not too far from water viscosity (1 cP). Higher viscosities could require lower speeds.

## Pipe speed - Metric units
Pipe diameter commercial | 25 | 40 | 50 | 65 | 80 | 100 | 125 | 150 | 200 | 250 | 300
| 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 5" | 6" | 8" | 10" | 12" | Calc sheet developed by Daniel de la Torre
Schedule | 10S |  | Stainless Steel | [8 empty] | Comments to: | DeLaTorreY.Eng@gmail.com
Internal Diam. | 27.86 | 42.76 | 54.76 | 66.9 | 82.8 | 108.2 | 134.48 | 161.48 | 211.58 | 264.7 | 314.74
Flow (m3/h) | Speed (m/s)
1 | 0.45566 | 0.19343 | 0.11795 | 0.079023 | 0.051588 | 0.03021 | 0.019557 | 0.013563 | 0.0079006 | 0.0050478 | 0.0035703
2.5 | 1.1392 | 0.48358 | 0.29486 | 0.19756 | 0.12897 | 0.075525 | 0.048891 | 0.033909 | 0.019751 | 0.012619 | 0.0089257
5 | 2.2783 | 0.96717 | 0.58973 | 0.39512 | 0.25794 | 0.15105 | 0.097783 | 0.067817 | 0.039503 | 0.025239 | 0.017851
7.5 | 3.4175 | 1.4508 | 0.88459 | 0.59268 | 0.38691 | 0.22658 | 0.14667 | 0.10173 | 0.059254 | 0.037858 | 0.026777
10 | 4.5566 | 1.9343 | 1.1795 | 0.79023 | 0.51588 | 0.3021 | 0.19557 | 0.13563 | 0.079006 | 0.050478 | 0.035703
12.5 | 5.6958 | 2.4179 | 1.4743 | 0.98779 | 0.64485 | 0.37763 | 0.24446 | 0.16954 | 0.098757 | 0.063097 | 0.044629
15 | 6.835 | 2.9015 | 1.7692 | 1.1854 | 0.77382 | 0.45315 | 0.29335 | 0.20345 | 0.11851 | 0.075717 | 0.053554
17.5 | 7.9741 | 3.3851 | 2.064 | 1.3829 | 0.90279 | 0.52868 | 0.34224 | 0.23736 | 0.13826 | 0.088336 | 0.06248
20 | 9.1133 | 3.8687 | 2.3589 | 1.5805 | 1.0318 | 0.6042 | 0.39113 | 0.27127 | 0.15801 | 0.10096 | 0.071406 |  |  | Nominal | Nominal | Outside |  | Schedule
22.5 | 10.2525 | 4.3523 | 2.6538 | 1.778 | 1.1607 | 0.67973 | 0.44002 | 0.30518 | 0.17776 | 0.11357 | 0.080332 |  |  | Pipe | Pipe | Diameter |  | 5S | 10S | 40S | 40 | 80S | 80
25 | 11.3916 | 4.8358 | 2.9486 | 1.9756 | 1.2897 | 0.75525 | 0.48891 | 0.33909 | 0.19751 | 0.12619 | 0.089257 |  |  | Size | Size | (mm) | (inches) | Wall Thickness
27.5 | 12.5308 | 5.3194 | 3.2435 | 2.1731 | 1.4187 | 0.83078 | 0.53781 | 0.37299 | 0.21727 | 0.13881 | 0.098183 |  |  | (mm) | (inches) |  |  | mm | mm | mm | mm | mm | mm
30 | 13.6699 | 5.803 | 3.5384 | 2.3707 | 1.5476 | 0.9063 | 0.5867 | 0.4069 | 0.23702 | 0.15143 | 0.10711 |  |  |  | 0.125 | 10.3 | 0.405 | - | 1.25 | 1.73 | 1.73 | 2.42 | 2.42
32.5 | 14.8091 | 6.2866 | 3.8332 | 2.5683 | 1.6766 | 0.98183 | 0.63559 | 0.44081 | 0.25677 | 0.16405 | 0.11603 |  |  |  | 0.25 | 13.7 | 0.540 | - | 1.66 | 2.24 | 2.24 | 3.03 | 3.03
35 | 15.9483 | 6.7702 | 4.1281 | 2.7658 | 1.8056 | 1.0574 | 0.68448 | 0.47472 | 0.27652 | 0.17667 | 0.12496 |  |  |  | 0.375 | 17.2 | 0.675 | - | 1.66 | 2.32 | 2.32 | 3.2 | 3.2
37.5 | 17.0874 | 7.2538 | 4.4229 | 2.9634 | 1.9345 | 1.1329 | 0.73337 | 0.50863 | 0.29627 | 0.18929 | 0.13389 |  |  |  | 0.5 | 21.3 | 0.840 | 1.65 | 2.11 | 2.77 | 2.77 | 3.74 | 3.74
40 | 18.2266 | 7.7373 | 4.7178 | 3.1609 | 2.0635 | 1.2084 | 0.78226 | 0.54254 | 0.31602 | 0.20191 | 0.14281 |  |  |  | 0.75 | 26.7 | 1.05 | 1.65 | 2.11 | 2.87 | 2.87 | 3.92 | 3.92
42.5 | 19.3658 | 8.2209 | 5.0127 | 3.3585 | 2.1925 | 1.2839 | 0.83115 | 0.57645 | 0.33577 | 0.21453 | 0.15174 |  |  | 25 | 1 | 33.4 | 1.315 | 1.65 | 2.77 | 3.38 | 3.38 | 4.55 | 4.55
45 | 20.5049 | 8.7045 | 5.3075 | 3.5561 | 2.3215 | 1.3595 | 0.88004 | 0.61036 | 0.35553 | 0.22715 | 0.16066 |  |  |  | 1.25 | 42.2 | 1.66 | 1.65 | 2.77 | 3.56 | 3.56 | 4.86 | 4.86
47.5 | 21.6441 | 9.1881 | 5.6024 | 3.7536 | 2.4504 | 1.435 | 0.92894 | 0.64426 | 0.37528 | 0.23977 | 0.16959 |  |  | 40 | 1.5 | 48.3 | 1.9 | 1.65 | 2.77 | 3.69 | 3.69 | 5.08 | 5.08
50 | 22.7832 | 9.6717 | 5.8973 | 3.9512 | 2.5794 | 1.5105 | 0.97783 | 0.67817 | 0.39503 | 0.25239 | 0.17851 |  |  | 50 | 2 | 60.3 | 2.375 | 1.65 | 2.77 | 3.92 | 3.92 | 5.54 | 5.54
52.5 | 23.9224 | 10.1553 | 6.1921 | 4.1487 | 2.7084 | 1.586 | 1.0267 | 0.71208 | 0.41478 | 0.26501 | 0.18744 |  |  | 65 | 2.5 | 73 | 2.875 | 2.11 | 3.05 | 5.16 | 5.16 | 7.01 | 7.01
55 | 25.0616 | 10.6389 | 6.487 | 4.3463 | 2.8373 | 1.6616 | 1.0756 | 0.74599 | 0.43453 | 0.27763 | 0.19637 |  |  | 80 | 3 | 88.9 | 3.5 | 2.11 | 3.05 | 5.49 | 5.49 | 7.62 | 7.62
57.5 | 26.2007 | 11.1224 | 6.7819 | 4.5438 | 2.9663 | 1.7371 | 1.1245 | 0.7799 | 0.45428 | 0.29025 | 0.20529 |  |  |  | 3.5 | 101.6 | 4 | 2.11 | 3.05 | 5.74 | 5.74 | 8.08 | 8.08
60 | 27.3399 | 11.606 | 7.0767 | 4.7414 | 3.0953 | 1.8126 | 1.1734 | 0.81381 | 0.47403 | 0.30287 | 0.21422 |  |  | 100 | 4 | 114.3 | 4.5 | 2.11 | 3.05 | 6.02 | 6.02 | 8.56 | 8.56
62.5 | 28.479 | 12.0896 | 7.3716 | 4.939 | 3.2242 | 1.8881 | 1.2223 | 0.84772 | 0.49379 | 0.31549 | 0.22314 |  |  | 125 | 5 | 141.3 | 5.563 | 2.77 | 3.41 | 6.56 | 6.56 | 9.53 | 9.53
65 | 29.6182 | 12.5732 | 7.6664 | 5.1365 | 3.3532 | 1.9637 | 1.2712 | 0.88162 | 0.51354 | 0.32811 | 0.23207 |  |  | 150 | 6 | 168.3 | 6.625 | 2.77 | 3.41 | 7.12 | 7.12 | 10.98 | 10.98
67.5 | 30.7574 | 13.0568 | 7.9613 | 5.3341 | 3.4822 | 2.0392 | 1.3201 | 0.91553 | 0.53329 | 0.34072 | 0.24099 |  |  | 200 | 8 | 219.1 | 8.625 | 2.77 | 3.76 | 8.18 | 8.18 | 12.7 | 12.7
70 | 31.8965 | 13.5404 | 8.2562 | 5.5316 | 3.6111 | 2.1147 | 1.369 | 0.94944 | 0.55304 | 0.35334 | 0.24992 |  |  | 250 | 10 | 273.1 | 1.075 | 3.41 | 4.2 | 9.28 | 9.28 | 12.7 | 12.7
72.5 | 33.0357 | 14.0239 | 8.551 | 5.7292 | 3.7401 | 2.1902 | 1.4178 | 0.98335 | 0.57279 | 0.36596 | 0.25885 |  |  | 300 | 12 | 323.9 | 1.275 | 3.97 | 4.58 | 9.53 | 9.53 | 12.7 | 12.7
75 | 34.1749 | 14.5075 | 8.8459 | 5.9268 | 3.8691 | 2.2658 | 1.4667 | 1.0173 | 0.59254 | 0.37858 | 0.26777
77.5 | 35.314 | 14.9911 | 9.1408 | 6.1243 | 3.9981 | 2.3413 | 1.5156 | 1.0512 | 0.61229 | 0.3912 | 0.2767
80 | 36.4532 | 15.4747 | 9.4356 | 6.3219 | 4.127 | 2.4168 | 1.5645 | 1.0851 | 0.63205 | 0.40382 | 0.28562
82.5 | 37.5923 | 15.9583 | 9.7305 | 6.5194 | 4.256 | 2.4923 | 1.6134 | 1.119 | 0.6518 | 0.41644 | 0.29455
85 | 38.7315 | 16.4419 | 10.0254 | 6.717 | 4.385 | 2.5679 | 1.6623 | 1.1529 | 0.67155 | 0.42906 | 0.30347
87.5 | 39.8707 | 16.9255 | 10.3202 | 6.9145 | 4.5139 | 2.6434 | 1.7112 | 1.1868 | 0.6913 | 0.44168 | 0.3124
90 | 41.0098 | 17.409 | 10.6151 | 7.1121 | 4.6429 | 2.7189 | 1.7601 | 1.2207 | 0.71105 | 0.4543 | 0.32133
92.5 | 42.149 | 17.8926 | 10.9099 | 7.3097 | 4.7719 | 2.7944 | 1.809 | 1.2546 | 0.7308 | 0.46692 | 0.33025
95 | 43.2881 | 18.3762 | 11.2048 | 7.5072 | 4.9008 | 2.87 | 1.8579 | 1.2885 | 0.75055 | 0.47954 | 0.33918
97.5 | 44.4273 | 18.8598 | 11.4997 | 7.7048 | 5.0298 | 2.9455 | 1.9068 | 1.3224 | 0.77031 | 0.49216 | 0.3481
100 | 45.5665 | 19.3434 | 11.7945 | 7.9023 | 5.1588 | 3.021 | 1.9557 | 1.3563 | 0.79006 | 0.50478 | 0.35703
110 | 50.1231 | 21.2777 | 12.974 | 8.6926 | 5.6747 | 3.3231 | 2.1512 | 1.492 | 0.86906 | 0.55525 | 0.39273
120 | 54.6798 | 23.212 | 14.1534 | 9.4828 | 6.1905 | 3.6252 | 2.3468 | 1.6276 | 0.94807 | 0.60573 | 0.42844
130 | 59.2364 | 25.1464 | 15.3329 | 10.273 | 6.7064 | 3.9273 | 2.5424 | 1.7632 | 1.0271 | 0.65621 | 0.46414
140 | 63.7931 | 27.0807 | 16.5123 | 11.0633 | 7.2223 | 4.2294 | 2.7379 | 1.8989 | 1.1061 | 0.70669 | 0.49984
150 | 68.3497 | 29.0151 | 17.6918 | 11.8535 | 7.7382 | 4.5315 | 2.9335 | 2.0345 | 1.1851 | 0.75717 | 0.53554
160 | 72.9064 | 30.9494 | 18.8713 | 12.6437 | 8.254 | 4.8336 | 3.129 | 2.1702 | 1.2641 | 0.80764 | 0.57125
170 | 77.463 | 32.8837 | 20.0507 | 13.434 | 8.7699 | 5.1357 | 3.3246 | 2.3058 | 1.3431 | 0.85812 | 0.60695
180 | 82.0196 | 34.8181 | 21.2302 | 14.2242 | 9.2858 | 5.4378 | 3.5202 | 2.4414 | 1.4221 | 0.9086 | 0.64265
190 | 86.5763 | 36.7524 | 22.4096 | 15.0144 | 9.8017 | 5.7399 | 3.7157 | 2.5771 | 1.5011 | 0.95908 | 0.67836
200 | 91.1329 | 38.6867 | 23.5891 | 15.8047 | 10.3176 | 6.042 | 3.9113 | 2.7127 | 1.5801 | 1.0096 | 0.71406
210 | 95.6896 | 40.6211 | 24.7685 | 16.5949 | 10.8334 | 6.3441 | 4.1069 | 2.8483 | 1.6591 | 1.06 | 0.74976
220 | 100.2462 | 42.5554 | 25.948 | 17.3851 | 11.3493 | 6.6462 | 4.3024 | 2.984 | 1.7381 | 1.1105 | 0.78546
230 | 104.8029 | 44.4898 | 27.1274 | 18.1754 | 11.8652 | 6.9483 | 4.498 | 3.1196 | 1.8171 | 1.161 | 0.82117
240 | 109.3595 | 46.4241 | 28.3069 | 18.9656 | 12.3811 | 7.2504 | 4.6936 | 3.2552 | 1.8961 | 1.2115 | 0.85687
250 | 113.9162 | 48.3584 | 29.4863 | 19.7558 | 12.8969 | 7.5525 | 4.8891 | 3.3909 | 1.9751 | 1.2619 | 0.89257
260 | 118.4728 | 50.2928 | 30.6658 | 20.5461 | 13.4128 | 7.8546 | 5.0847 | 3.5265 | 2.0541 | 1.3124 | 0.92828
270 | 123.0295 | 52.2271 | 31.8452 | 21.3363 | 13.9287 | 8.1567 | 5.2803 | 3.6621 | 2.1332 | 1.3629 | 0.96398
280 | 127.5861 | 54.1614 | 33.0247 | 22.1265 | 14.4446 | 8.4588 | 5.4758 | 3.7978 | 2.2122 | 1.4134 | 0.99968
290 | 132.1428 | 56.0958 | 34.2041 | 22.9168 | 14.9605 | 8.7609 | 5.6714 | 3.9334 | 2.2912 | 1.4639 | 1.0354
300 | 136.6994 | 58.0301 | 35.3836 | 23.707 | 15.4763 | 9.063 | 5.867 | 4.069 | 2.3702 | 1.5143 | 1.0711
310 | 141.2561 | 59.9645 | 36.5631 | 24.4972 | 15.9922 | 9.3652 | 6.0625 | 4.2047 | 2.4492 | 1.5648 | 1.1068
320 | 145.8127 | 61.8988 | 37.7425 | 25.2875 | 16.5081 | 9.6673 | 6.2581 | 4.3403 | 2.5282 | 1.6153 | 1.1425
330 | 150.3694 | 63.8331 | 38.922 | 26.0777 | 17.024 | 9.9694 | 6.4537 | 4.4759 | 2.6072 | 1.6658 | 1.1782
340 | 154.926 | 65.7675 | 40.1014 | 26.8679 | 17.5398 | 10.2715 | 6.6492 | 4.6116 | 2.6862 | 1.7162 | 1.2139
350 | 159.4826 | 67.7018 | 41.2809 | 27.6582 | 18.0557 | 10.5736 | 6.8448 | 4.7472 | 2.7652 | 1.7667 | 1.2496
360 | 164.0393 | 69.6361 | 42.4603 | 28.4484 | 18.5716 | 10.8757 | 7.0404 | 4.8828 | 2.8442 | 1.8172 | 1.2853
370 | 168.5959 | 71.5705 | 43.6398 | 29.2386 | 19.0875 | 11.1778 | 7.2359 | 5.0185 | 2.9232 | 1.8677 | 1.321
380 | 173.1526 | 73.5048 | 44.8192 | 30.0289 | 19.6034 | 11.4799 | 7.4315 | 5.1541 | 3.0022 | 1.9182 | 1.3567
390 | 177.7092 | 75.4392 | 45.9987 | 30.8191 | 20.1192 | 11.782 | 7.6271 | 5.2897 | 3.0812 | 1.9686 | 1.3924
400 | 182.2659 | 77.3735 | 47.1781 | 31.6093 | 20.6351 | 12.0841 | 7.8226 | 5.4254 | 3.1602 | 2.0191 | 1.4281
410 | 186.8225 | 79.3078 | 48.3576 | 32.3996 | 21.151 | 12.3862 | 8.0182 | 5.561 | 3.2392 | 2.0696 | 1.4638
420 | 191.3792 | 81.2422 | 49.537 | 33.1898 | 21.6669 | 12.6883 | 8.2138 | 5.6966 | 3.3182 | 2.1201 | 1.4995
430 | 195.9358 | 83.1765 | 50.7165 | 33.98 | 22.1828 | 12.9904 | 8.4093 | 5.8323 | 3.3972 | 2.1705 | 1.5352
440 | 200.4925 | 85.1108 | 51.8959 | 34.7703 | 22.6986 | 13.2925 | 8.6049 | 5.9679 | 3.4763 | 2.221 | 1.5709
450 | 205.0491 | 87.0452 | 53.0754 | 35.5605 | 23.2145 | 13.5946 | 8.8004 | 6.1036 | 3.5553 | 2.2715 | 1.6066
460 | 209.6058 | 88.9795 | 54.2549 | 36.3507 | 23.7304 | 13.8967 | 8.996 | 6.2392 | 3.6343 | 2.322 | 1.6423
470 | 214.1624 | 90.9139 | 55.4343 | 37.141 | 24.2463 | 14.1988 | 9.1916 | 6.3748 | 3.7133 | 2.3725 | 1.678
480 | 218.7191 | 92.8482 | 56.6138 | 37.9312 | 24.7621 | 14.5009 | 9.3871 | 6.5105 | 3.7923 | 2.4229 | 1.7137
490 | 223.2757 | 94.7825 | 57.7932 | 38.7214 | 25.278 | 14.803 | 9.5827 | 6.6461 | 3.8713 | 2.4734 | 1.7494
500 | 227.8324 | 96.7169 | 58.9727 | 39.5117 | 25.7939 | 15.1051 | 9.7783 | 6.7817 | 3.9503 | 2.5239 | 1.7851
510 | 232.389 | 98.6512 | 60.1521 | 40.3019 | 26.3098 | 15.4072 | 9.9738 | 6.9174 | 4.0293 | 2.5744 | 1.8208
520 | 236.9456 | 100.5855 | 61.3316 | 41.0921 | 26.8257 | 15.7093 | 10.1694 | 7.053 | 4.1083 | 2.6248 | 1.8566
530 | 241.5023 | 102.5199 | 62.511 | 41.8824 | 27.3415 | 16.0114 | 10.365 | 7.1886 | 4.1873 | 2.6753 | 1.8923
540 | 246.0589 | 104.4542 | 63.6905 | 42.6726 | 27.8574 | 16.3135 | 10.5605 | 7.3243 | 4.2663 | 2.7258 | 1.928
550 | 250.6156 | 106.3886 | 64.8699 | 43.4628 | 28.3733 | 16.6156 | 10.7561 | 7.4599 | 4.3453 | 2.7763 | 1.9637
560 | 255.1722 | 108.3229 | 66.0494 | 44.2531 | 28.8892 | 16.9177 | 10.9517 | 7.5955 | 4.4243 | 2.8268 | 1.9994
570 | 259.7289 | 110.2572 | 67.2288 | 45.0433 | 29.405 | 17.2198 | 11.1472 | 7.7312 | 4.5033 | 2.8772 | 2.0351
580 | 264.2855 | 112.1916 | 68.4083 | 45.8335 | 29.9209 | 17.5219 | 11.3428 | 7.8668 | 4.5823 | 2.9277 | 2.0708
590 | 268.8422 | 114.1259 | 69.5877 | 46.6238 | 30.4368 | 17.824 | 11.5384 | 8.0024 | 4.6613 | 2.9782 | 2.1065
600 | 273.3988 | 116.0602 | 70.7672 | 47.414 | 30.9527 | 18.1261 | 11.7339 | 8.1381 | 4.7403 | 3.0287 | 2.1422
610 | 277.9555 | 117.9946 | 71.9466 | 48.2042 | 31.4686 | 18.4282 | 11.9295 | 8.2737 | 4.8193 | 3.0791 | 2.1779
620 | 282.5121 | 119.9289 | 73.1261 | 48.9945 | 31.9844 | 18.7303 | 12.1251 | 8.4093 | 4.8984 | 3.1296 | 2.2136
630 | 287.0688 | 121.8633 | 74.3056 | 49.7847 | 32.5003 | 19.0324 | 12.3206 | 8.545 | 4.9774 | 3.1801 | 2.2493
640 | 291.6254 | 123.7976 | 75.485 | 50.5749 | 33.0162 | 19.3345 | 12.5162 | 8.6806 | 5.0564 | 3.2306 | 2.285
650 | 296.1821 | 125.7319 | 76.6645 | 51.3652 | 33.5321 | 19.6366 | 12.7118 | 8.8162 | 5.1354 | 3.2811 | 2.3207
660 | 300.7387 | 127.6663 | 77.8439 | 52.1554 | 34.0479 | 19.9387 | 12.9073 | 8.9519 | 5.2144 | 3.3315 | 2.3564
670 | 305.2954 | 129.6006 | 79.0234 | 52.9456 | 34.5638 | 20.2408 | 13.1029 | 9.0875 | 5.2934 | 3.382 | 2.3921
680 | 309.852 | 131.5349 | 80.2028 | 53.7359 | 35.0797 | 20.5429 | 13.2985 | 9.2231 | 5.3724 | 3.4325 | 2.4278
690 | 314.4086 | 133.4693 | 81.3823 | 54.5261 | 35.5956 | 20.845 | 13.494 | 9.3588 | 5.4514 | 3.483 | 2.4635
700 | 318.9653 | 135.4036 | 82.5617 | 55.3163 | 36.1115 | 21.1471 | 13.6896 | 9.4944 | 5.5304 | 3.5334 | 2.4992
710 | 323.5219 | 137.338 | 83.7412 | 56.1066 | 36.6273 | 21.4492 | 13.8851 | 9.63 | 5.6094 | 3.5839 | 2.5349
720 | 328.0786 | 139.2723 | 84.9206 | 56.8968 | 37.1432 | 21.7513 | 14.0807 | 9.7657 | 5.6884 | 3.6344 | 2.5706
730 | 332.6352 | 141.2066 | 86.1001 | 57.687 | 37.6591 | 22.0534 | 14.2763 | 9.9013 | 5.7674 | 3.6849 | 2.6063
740 | 337.1919 | 143.141 | 87.2795 | 58.4773 | 38.175 | 22.3555 | 14.4718 | 10.037 | 5.8464 | 3.7354 | 2.642
750 | 341.7485 | 145.0753 | 88.459 | 59.2675 | 38.6908 | 22.6576 | 14.6674 | 10.1726 | 5.9254 | 3.7858 | 2.6777
760 | 346.3052 | 147.0096 | 89.6384 | 60.0577 | 39.2067 | 22.9597 | 14.863 | 10.3082 | 6.0044 | 3.8363 | 2.7134
770 | 350.8618 | 148.944 | 90.8179 | 60.848 | 39.7226 | 23.2618 | 15.0585 | 10.4439 | 6.0834 | 3.8868 | 2.7491
780 | 355.4185 | 150.8783 | 91.9974 | 61.6382 | 40.2385 | 23.5639 | 15.2541 | 10.5795 | 6.1624 | 3.9373 | 2.7848
790 | 359.9751 | 152.8127 | 93.1768 | 62.4284 | 40.7544 | 23.866 | 15.4497 | 10.7151 | 6.2414 | 3.9877 | 2.8205
800 | 364.5318 | 154.747 | 94.3563 | 63.2187 | 41.2702 | 24.1681 | 15.6452 | 10.8508 | 6.3205 | 4.0382 | 2.8562
810 | 369.0884 | 156.6813 | 95.5357 | 64.0089 | 41.7861 | 24.4702 | 15.8408 | 10.9864 | 6.3995 | 4.0887 | 2.8919
820 | 373.6451 | 158.6157 | 96.7152 | 64.7991 | 42.302 | 24.7723 | 16.0364 | 11.122 | 6.4785 | 4.1392 | 2.9276
830 | 378.2017 | 160.55 | 97.8946 | 65.5894 | 42.8179 | 25.0744 | 16.2319 | 11.2577 | 6.5575 | 4.1897 | 2.9633
840 | 382.7584 | 162.4843 | 99.0741 | 66.3796 | 43.3337 | 25.3765 | 16.4275 | 11.3933 | 6.6365 | 4.2401 | 2.999
850 | 387.315 | 164.4187 | 100.2535 | 67.1698 | 43.8496 | 25.6786 | 16.6231 | 11.5289 | 6.7155 | 4.2906 | 3.0347
860 | 391.8716 | 166.353 | 101.433 | 67.9601 | 44.3655 | 25.9807 | 16.8186 | 11.6646 | 6.7945 | 4.3411 | 3.0705
870 | 396.4283 | 168.2874 | 102.6124 | 68.7503 | 44.8814 | 26.2828 | 17.0142 | 11.8002 | 6.8735 | 4.3916 | 3.1062
880 | 400.9849 | 170.2217 | 103.7919 | 69.5405 | 45.3973 | 26.5849 | 17.2098 | 11.9358 | 6.9525 | 4.442 | 3.1419
890 | 405.5416 | 172.156 | 104.9713 | 70.3308 | 45.9131 | 26.887 | 17.4053 | 12.0715 | 7.0315 | 4.4925 | 3.1776
900 | 410.0982 | 174.0904 | 106.1508 | 71.121 | 46.429 | 27.1891 | 17.6009 | 12.2071 | 7.1105 | 4.543 | 3.2133
910 | 414.6549 | 176.0247 | 107.3302 | 71.9112 | 46.9449 | 27.4913 | 17.7965 | 12.3427 | 7.1895 | 4.5935 | 3.249
920 | 419.2115 | 177.959 | 108.5097 | 72.7015 | 47.4608 | 27.7934 | 17.992 | 12.4784 | 7.2685 | 4.644 | 3.2847
930 | 423.7682 | 179.8934 | 109.6892 | 73.4917 | 47.9766 | 28.0955 | 18.1876 | 12.614 | 7.3475 | 4.6944 | 3.3204
940 | 428.3248 | 181.8277 | 110.8686 | 74.2819 | 48.4925 | 28.3976 | 18.3832 | 12.7496 | 7.4265 | 4.7449 | 3.3561
950 | 432.8815 | 183.7621 | 112.0481 | 75.0722 | 49.0084 | 28.6997 | 18.5787 | 12.8853 | 7.5055 | 4.7954 | 3.3918
960 | 437.4381 | 185.6964 | 113.2275 | 75.8624 | 49.5243 | 29.0018 | 18.7743 | 13.0209 | 7.5845 | 4.8459 | 3.4275
970 | 441.9948 | 187.6307 | 114.407 | 76.6526 | 50.0402 | 29.3039 | 18.9699 | 13.1565 | 7.6636 | 4.8963 | 3.4632
980 | 446.5514 | 189.5651 | 115.5864 | 77.4429 | 50.556 | 29.606 | 19.1654 | 13.2922 | 7.7426 | 4.9468 | 3.4989
990 | 451.1081 | 191.4994 | 116.7659 | 78.2331 | 51.0719 | 29.9081 | 19.361 | 13.4278 | 7.8216 | 4.9973 | 3.5346
1000 | 455.6647 | 193.4337 | 117.9453 | 79.0233 | 51.5878 | 30.2102 | 19.5565 | 13.5634 | 7.9006 | 5.0478 | 3.5703

## Pipe speed - Imperial units
Pipe diameter commercial |  | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 5" | 6" | 8" | 10" | 12"
|  | 25 | 40 | 50 | 65 | 80 | 100 | 125 | 150 | 200 | 250 | 300 | Calc sheet developed by Daniel de la Torre
Schedule |  | 10S |  | Stainless Steel | [8 empty] | Comments to: | DeLaTorreY.Eng@gmail.com
Internal Diam. |  | 1.0969 | 1.6835 | 2.1559 | 2.6339 | 3.2598 | 4.2598 | 5.2945 | 6.3575 | 8.3299 | 10.4213 | 12.3913
Flow (US gpm) | Flow (UK gpm) | Speed (ft/s)
5 | 4.165 | 1.6977 | 0.72069 | 0.43944 | 0.29442 | 0.1922 | 0.11256 | 0.072863 | 0.050534 | 0.029436 | 0.018807 | 0.013302
10 | 8.33 | 3.3954 | 1.4414 | 0.87888 | 0.58885 | 0.38441 | 0.22511 | 0.14573 | 0.10107 | 0.058872 | 0.037614 | 0.026604
20 | 16.66 | 6.7908 | 2.8828 | 1.7578 | 1.1777 | 0.76882 | 0.45023 | 0.29145 | 0.20214 | 0.11774 | 0.075228 | 0.053209
30 | 24.99 | 10.1862 | 4.3242 | 2.6366 | 1.7665 | 1.1532 | 0.67534 | 0.43718 | 0.30321 | 0.17661 | 0.11284 | 0.079813
40 | 33.32 | 13.5817 | 5.7655 | 3.5155 | 2.3554 | 1.5376 | 0.90045 | 0.58291 | 0.40428 | 0.23549 | 0.15046 | 0.10642
50 | 41.65 | 16.9771 | 7.2069 | 4.3944 | 2.9442 | 1.922 | 1.1256 | 0.72863 | 0.50534 | 0.29436 | 0.18807 | 0.13302
60 | 49.98 | 20.3725 | 8.6483 | 5.2733 | 3.5331 | 2.3065 | 1.3507 | 0.87436 | 0.60641 | 0.35323 | 0.22568 | 0.15963
70 | 58.31 | 23.7679 | 10.0897 | 6.1521 | 4.1219 | 2.6909 | 1.5758 | 1.0201 | 0.70748 | 0.4121 | 0.2633 | 0.18623
80 | 66.64 | 27.1633 | 11.5311 | 7.031 | 4.7108 | 3.0753 | 1.8009 | 1.1658 | 0.80855 | 0.47097 | 0.30091 | 0.21283 |  |  | Nominal | Nominal | Outside |  | Schedule
90 | 74.97 | 30.5587 | 12.9725 | 7.9099 | 5.2996 | 3.4597 | 2.026 | 1.3115 | 0.90962 | 0.52984 | 0.33852 | 0.23944 |  |  | Pipe | Pipe | Diameter |  | 5S | 10S | 40S | 40 | 80S | 80
100 | 83.3 | 33.9542 | 14.4138 | 8.7888 | 5.8885 | 3.8441 | 2.2511 | 1.4573 | 1.0107 | 0.58872 | 0.37614 | 0.26604 |  |  | Size | Size | (mm) | (inches) | Wall Thickness
110 | 91.63 | 37.3496 | 15.8552 | 9.6677 | 6.4773 | 4.2285 | 2.4762 | 1.603 | 1.1118 | 0.64759 | 0.41375 | 0.29265 |  |  | (mm) | (inches) |  |  | mm | mm | mm | mm | mm | mm
120 | 99.96 | 40.745 | 17.2966 | 10.5465 | 7.0662 | 4.6129 | 2.7014 | 1.7487 | 1.2128 | 0.70646 | 0.45137 | 0.31925 |  |  |  | 0.125 | 10.3 | 0.405 | - | 1.25 | 1.73 | 1.73 | 2.42 | 2.42
130 | 108.29 | 44.1404 | 18.738 | 11.4254 | 7.655 | 4.9973 | 2.9265 | 1.8945 | 1.3139 | 0.76533 | 0.48898 | 0.34586 |  |  |  | 0.25 | 13.7 | 0.540 | - | 1.66 | 2.24 | 2.24 | 3.03 | 3.03
140 | 116.62 | 47.5358 | 20.1794 | 12.3043 | 8.2439 | 5.3817 | 3.1516 | 2.0402 | 1.415 | 0.8242 | 0.52659 | 0.37246 |  |  |  | 0.375 | 17.2 | 0.675 | - | 1.66 | 2.32 | 2.32 | 3.2 | 3.2
150 | 124.95 | 50.9312 | 21.6208 | 13.1832 | 8.8327 | 5.7661 | 3.3767 | 2.1859 | 1.516 | 0.88307 | 0.56421 | 0.39906 |  |  |  | 0.5 | 21.3 | 0.840 | 1.65 | 2.11 | 2.77 | 2.77 | 3.74 | 3.74
160 | 133.28 | 54.3267 | 23.0622 | 14.062 | 9.4216 | 6.1506 | 3.6018 | 2.3316 | 1.6171 | 0.94195 | 0.60182 | 0.42567 |  |  |  | 0.75 | 26.7 | 1.05 | 1.65 | 2.11 | 2.87 | 2.87 | 3.92 | 3.92
170 | 141.61 | 57.7221 | 24.5035 | 14.9409 | 10.0104 | 6.535 | 3.8269 | 2.4774 | 1.7182 | 1.0008 | 0.63943 | 0.45227 |  |  | 25 | 1 | 33.4 | 1.315 | 1.65 | 2.77 | 3.38 | 3.38 | 4.55 | 4.55
180 | 149.94 | 61.1175 | 25.9449 | 15.8198 | 10.5993 | 6.9194 | 4.052 | 2.6231 | 1.8192 | 1.0597 | 0.67705 | 0.47888 |  |  |  | 1.25 | 42.2 | 1.66 | 1.65 | 2.77 | 3.56 | 3.56 | 4.86 | 4.86
190 | 158.27 | 64.5129 | 27.3863 | 16.6987 | 11.1881 | 7.3038 | 4.2771 | 2.7688 | 1.9203 | 1.1186 | 0.71466 | 0.50548 |  |  | 40 | 1.5 | 48.3 | 1.9 | 1.65 | 2.77 | 3.69 | 3.69 | 5.08 | 5.08
200 | 166.6 | 67.9083 | 28.8277 | 17.5776 | 11.777 | 7.6882 | 4.5023 | 2.9145 | 2.0214 | 1.1774 | 0.75228 | 0.53209 |  |  | 50 | 2 | 60.3 | 2.375 | 1.65 | 2.77 | 3.92 | 3.92 | 5.54 | 5.54
210 | 174.93 | 71.3037 | 30.2691 | 18.4564 | 12.3658 | 8.0726 | 4.7274 | 3.0603 | 2.1224 | 1.2363 | 0.78989 | 0.55869 |  |  | 65 | 2.5 | 73 | 2.875 | 2.11 | 3.05 | 5.16 | 5.16 | 7.01 | 7.01
220 | 183.26 | 74.6992 | 31.7105 | 19.3353 | 12.9546 | 8.457 | 4.9525 | 3.206 | 2.2235 | 1.2952 | 0.8275 | 0.58529 |  |  | 80 | 3 | 88.9 | 3.5 | 2.11 | 3.05 | 5.49 | 5.49 | 7.62 | 7.62
230 | 191.59 | 78.0946 | 33.1518 | 20.2142 | 13.5435 | 8.8414 | 5.1776 | 3.3517 | 2.3246 | 1.354 | 0.86512 | 0.6119 |  |  |  | 3.5 | 101.6 | 4 | 2.11 | 3.05 | 5.74 | 5.74 | 8.08 | 8.08
240 | 199.92 | 81.49 | 34.5932 | 21.0931 | 14.1323 | 9.2258 | 5.4027 | 3.4974 | 2.4257 | 1.4129 | 0.90273 | 0.6385 |  |  | 100 | 4 | 114.3 | 4.5 | 2.11 | 3.05 | 6.02 | 6.02 | 8.56 | 8.56
250 | 208.25 | 84.8854 | 36.0346 | 21.9719 | 14.7212 | 9.6102 | 5.6278 | 3.6432 | 2.5267 | 1.4718 | 0.94035 | 0.66511 |  |  | 125 | 5 | 141.3 | 5.563 | 2.77 | 3.41 | 6.56 | 6.56 | 9.53 | 9.53
260 | 216.58 | 88.2808 | 37.476 | 22.8508 | 15.31 | 9.9947 | 5.8529 | 3.7889 | 2.6278 | 1.5307 | 0.97796 | 0.69171 |  |  | 150 | 6 | 168.3 | 6.625 | 2.77 | 3.41 | 7.12 | 7.12 | 10.98 | 10.98
270 | 224.91 | 91.6762 | 38.9174 | 23.7297 | 15.8989 | 10.3791 | 6.0781 | 3.9346 | 2.7289 | 1.5895 | 1.0156 | 0.71832 |  |  | 200 | 8 | 219.1 | 8.625 | 2.77 | 3.76 | 8.18 | 8.18 | 12.7 | 12.7
280 | 233.24 | 95.0717 | 40.3588 | 24.6086 | 16.4877 | 10.7635 | 6.3032 | 4.0804 | 2.8299 | 1.6484 | 1.0532 | 0.74492 |  |  | 250 | 10 | 273.1 | 1.075 | 3.41 | 4.2 | 9.28 | 9.28 | 12.7 | 12.7
290 | 241.57 | 98.4671 | 41.8001 | 25.4874 | 17.0766 | 11.1479 | 6.5283 | 4.2261 | 2.931 | 1.7073 | 1.0908 | 0.77152 |  |  | 300 | 12 | 323.9 | 1.275 | 3.97 | 4.58 | 9.53 | 9.53 | 12.7 | 12.7
300 | 249.9 | 101.8625 | 43.2415 | 26.3663 | 17.6654 | 11.5323 | 6.7534 | 4.3718 | 3.0321 | 1.7661 | 1.1284 | 0.79813
310 | 258.23 | 105.2579 | 44.6829 | 27.2452 | 18.2543 | 11.9167 | 6.9785 | 4.5175 | 3.1331 | 1.825 | 1.166 | 0.82473
320 | 266.56 | 108.6533 | 46.1243 | 28.1241 | 18.8431 | 12.3011 | 7.2036 | 4.6633 | 3.2342 | 1.8839 | 1.2036 | 0.85134
330 | 274.89 | 112.0487 | 47.5657 | 29.003 | 19.432 | 12.6855 | 7.4287 | 4.809 | 3.3353 | 1.9428 | 1.2413 | 0.87794
340 | 283.22 | 115.4441 | 49.0071 | 29.8818 | 20.0208 | 13.0699 | 7.6538 | 4.9547 | 3.4363 | 2.0016 | 1.2789 | 0.90455
350 | 291.55 | 118.8396 | 50.4485 | 30.7607 | 20.6097 | 13.4543 | 7.879 | 5.1004 | 3.5374 | 2.0605 | 1.3165 | 0.93115
360 | 299.88 | 122.235 | 51.8898 | 31.6396 | 21.1985 | 13.8388 | 8.1041 | 5.2462 | 3.6385 | 2.1194 | 1.3541 | 0.95775
370 | 308.21 | 125.6304 | 53.3312 | 32.5185 | 21.7874 | 14.2232 | 8.3292 | 5.3919 | 3.7396 | 2.1783 | 1.3917 | 0.98436
380 | 316.54 | 129.0258 | 54.7726 | 33.3973 | 22.3762 | 14.6076 | 8.5543 | 5.5376 | 3.8406 | 2.2371 | 1.4293 | 1.011
390 | 324.87 | 132.4212 | 56.214 | 34.2762 | 22.9651 | 14.992 | 8.7794 | 5.6834 | 3.9417 | 2.296 | 1.4669 | 1.0376
400 | 333.2 | 135.8166 | 57.6554 | 35.1551 | 23.5539 | 15.3764 | 9.0045 | 5.8291 | 4.0428 | 2.3549 | 1.5046 | 1.0642
440 | 366.52 | 149.3983 | 63.4209 | 38.6706 | 25.9093 | 16.914 | 9.905 | 6.412 | 4.447 | 2.5904 | 1.655 | 1.1706
480 | 399.84 | 162.98 | 69.1865 | 42.1861 | 28.2647 | 18.4517 | 10.8054 | 6.9949 | 4.8513 | 2.8258 | 1.8055 | 1.277
520 | 433.16 | 176.5616 | 74.952 | 45.7016 | 30.6201 | 19.9893 | 11.7059 | 7.5778 | 5.2556 | 3.0613 | 1.9559 | 1.3834
560 | 466.48 | 190.1433 | 80.7175 | 49.2171 | 32.9755 | 21.527 | 12.6063 | 8.1607 | 5.6599 | 3.2968 | 2.1064 | 1.4898
600 | 499.8 | 203.725 | 86.4831 | 52.7327 | 35.3309 | 23.0646 | 13.5068 | 8.7436 | 6.0641 | 3.5323 | 2.2568 | 1.5963
640 | 533.12 | 217.3066 | 92.2486 | 56.2482 | 37.6863 | 24.6022 | 14.4072 | 9.3265 | 6.4684 | 3.7678 | 2.4073 | 1.7027
680 | 566.44 | 230.8883 | 98.0141 | 59.7637 | 40.0416 | 26.1399 | 15.3077 | 9.9094 | 6.8727 | 4.0033 | 2.5577 | 1.8091
720 | 599.76 | 244.47 | 103.7797 | 63.2792 | 42.397 | 27.6775 | 16.2081 | 10.4923 | 7.277 | 4.2388 | 2.7082 | 1.9155
760 | 633.08 | 258.0516 | 109.5452 | 66.7947 | 44.7524 | 29.2152 | 17.1086 | 11.0752 | 7.6812 | 4.4742 | 2.8586 | 2.0219
800 | 666.4 | 271.6333 | 115.3108 | 70.3102 | 47.1078 | 30.7528 | 18.009 | 11.6582 | 8.0855 | 4.7097 | 3.0091 | 2.1283
840 | 699.72 | 285.215 | 121.0763 | 73.8257 | 49.4632 | 32.2904 | 18.9095 | 12.2411 | 8.4898 | 4.9452 | 3.1596 | 2.2348
880 | 733.04 | 298.7966 | 126.8418 | 77.3412 | 51.8186 | 33.8281 | 19.81 | 12.824 | 8.8941 | 5.1807 | 3.31 | 2.3412
920 | 766.36 | 312.3783 | 132.6074 | 80.8567 | 54.174 | 35.3657 | 20.7104 | 13.4069 | 9.2983 | 5.4162 | 3.4605 | 2.4476
960 | 799.68 | 325.9599 | 138.3729 | 84.3722 | 56.5294 | 36.9033 | 21.6109 | 13.9898 | 9.7026 | 5.6517 | 3.6109 | 2.554
1000 | 833 | 339.5416 | 144.1384 | 87.8878 | 58.8848 | 38.441 | 22.5113 | 14.5727 | 10.1069 | 5.8872 | 3.7614 | 2.6604
1040 | 866.32 | 353.1233 | 149.904 | 91.4033 | 61.2402 | 39.9786 | 23.4118 | 15.1556 | 10.5112 | 6.1226 | 3.9118 | 2.7668
1080 | 899.64 | 366.7049 | 155.6695 | 94.9188 | 63.5956 | 41.5163 | 24.3122 | 15.7385 | 10.9154 | 6.3581 | 4.0623 | 2.8733
1120 | 932.96 | 380.2866 | 161.4351 | 98.4343 | 65.9509 | 43.0539 | 25.2127 | 16.3214 | 11.3197 | 6.5936 | 4.2127 | 2.9797
1160 | 966.28 | 393.8683 | 167.2006 | 101.9498 | 68.3063 | 44.5915 | 26.1131 | 16.9043 | 11.724 | 6.8291 | 4.3632 | 3.0861
1200 | 999.6 | 407.4499 | 172.9661 | 105.4653 | 70.6617 | 46.1292 | 27.0136 | 17.4872 | 12.1283 | 7.0646 | 4.5137 | 3.1925
1240 | 1032.92 | 421.0316 | 178.7317 | 108.9808 | 73.0171 | 47.6668 | 27.914 | 18.0701 | 12.5325 | 7.3001 | 4.6641 | 3.2989
1280 | 1066.24 | 434.6133 | 184.4972 | 112.4963 | 75.3725 | 49.2045 | 28.8145 | 18.653 | 12.9368 | 7.5356 | 4.8146 | 3.4053
1320 | 1099.56 | 448.1949 | 190.2627 | 116.0118 | 77.7279 | 50.7421 | 29.7149 | 19.236 | 13.3411 | 7.7711 | 4.965 | 3.5118
1360 | 1132.88 | 461.7766 | 196.0283 | 119.5273 | 80.0833 | 52.2797 | 30.6154 | 19.8189 | 13.7454 | 8.0065 | 5.1155 | 3.6182
1400 | 1166.2 | 475.3583 | 201.7938 | 123.0429 | 82.4387 | 53.8174 | 31.5158 | 20.4018 | 14.1497 | 8.242 | 5.2659 | 3.7246
1440 | 1199.52 | 488.9399 | 207.5594 | 126.5584 | 84.7941 | 55.355 | 32.4163 | 20.9847 | 14.5539 | 8.4775 | 5.4164 | 3.831
1480 | 1232.84 | 502.5216 | 213.3249 | 130.0739 | 87.1495 | 56.8927 | 33.3167 | 21.5676 | 14.9582 | 8.713 | 5.5668 | 3.9374
1520 | 1266.16 | 516.1033 | 219.0904 | 133.5894 | 89.5049 | 58.4303 | 34.2172 | 22.1505 | 15.3625 | 8.9485 | 5.7173 | 4.0438
1560 | 1299.48 | 529.6849 | 224.856 | 137.1049 | 91.8602 | 59.9679 | 35.1176 | 22.7334 | 15.7668 | 9.184 | 5.8678 | 4.1503
1600 | 1332.8 | 543.2666 | 230.6215 | 140.6204 | 94.2156 | 61.5056 | 36.0181 | 23.3163 | 16.171 | 9.4195 | 6.0182 | 4.2567
1640 | 1366.12 | 556.8482 | 236.3871 | 144.1359 | 96.571 | 63.0432 | 36.9185 | 23.8992 | 16.5753 | 9.6549 | 6.1687 | 4.3631
1680 | 1399.44 | 570.4299 | 242.1526 | 147.6514 | 98.9264 | 64.5809 | 37.819 | 24.4821 | 16.9796 | 9.8904 | 6.3191 | 4.4695
1720 | 1432.76 | 584.0116 | 247.9181 | 151.1669 | 101.2818 | 66.1185 | 38.7194 | 25.065 | 17.3839 | 10.1259 | 6.4696 | 4.5759
1760 | 1466.08 | 597.5932 | 253.6837 | 154.6824 | 103.6372 | 67.6561 | 39.6199 | 25.6479 | 17.7881 | 10.3614 | 6.62 | 4.6824
1800 | 1499.4 | 611.1749 | 259.4492 | 158.198 | 105.9926 | 69.1938 | 40.5204 | 26.2308 | 18.1924 | 10.5969 | 6.7705 | 4.7888
1840 | 1532.72 | 624.7566 | 265.2147 | 161.7135 | 108.348 | 70.7314 | 41.4208 | 26.8138 | 18.5967 | 10.8324 | 6.9209 | 4.8952
1880 | 1566.04 | 638.3382 | 270.9803 | 165.229 | 110.7034 | 72.2691 | 42.3213 | 27.3967 | 19.001 | 11.0679 | 7.0714 | 5.0016
1920 | 1599.36 | 651.9199 | 276.7458 | 168.7445 | 113.0588 | 73.8067 | 43.2217 | 27.9796 | 19.4052 | 11.3034 | 7.2219 | 5.108
1960 | 1632.68 | 665.5016 | 282.5114 | 172.26 | 115.4142 | 75.3443 | 44.1222 | 28.5625 | 19.8095 | 11.5388 | 7.3723 | 5.2144
2000 | 1666 | 679.0832 | 288.2769 | 175.7755 | 117.7695 | 76.882 | 45.0226 | 29.1454 | 20.2138 | 11.7743 | 7.5228 | 5.3209
2040 | 1699.32 | 692.6649 | 294.0424 | 179.291 | 120.1249 | 78.4196 | 45.9231 | 29.7283 | 20.6181 | 12.0098 | 7.6732 | 5.4273
2080 | 1732.64 | 706.2466 | 299.808 | 182.8065 | 122.4803 | 79.9573 | 46.8235 | 30.3112 | 21.0223 | 12.2453 | 7.8237 | 5.5337
2120 | 1765.96 | 719.8282 | 305.5735 | 186.322 | 124.8357 | 81.4949 | 47.724 | 30.8941 | 21.4266 | 12.4808 | 7.9741 | 5.6401
2160 | 1799.28 | 733.4099 | 311.339 | 189.8375 | 127.1911 | 83.0325 | 48.6244 | 31.477 | 21.8309 | 12.7163 | 8.1246 | 5.7465
2200 | 1832.6 | 746.9915 | 317.1046 | 193.3531 | 129.5465 | 84.5702 | 49.5249 | 32.0599 | 22.2352 | 12.9518 | 8.275 | 5.8529
2240 | 1865.92 | 760.5732 | 322.8701 | 196.8686 | 131.9019 | 86.1078 | 50.4253 | 32.6428 | 22.6394 | 13.1872 | 8.4255 | 5.9594
2280 | 1899.24 | 774.1549 | 328.6357 | 200.3841 | 134.2573 | 87.6455 | 51.3258 | 33.2257 | 23.0437 | 13.4227 | 8.5759 | 6.0658
2320 | 1932.56 | 787.7365 | 334.4012 | 203.8996 | 136.6127 | 89.1831 | 52.2262 | 33.8086 | 23.448 | 13.6582 | 8.7264 | 6.1722
2360 | 1965.88 | 801.3182 | 340.1667 | 207.4151 | 138.9681 | 90.7207 | 53.1267 | 34.3916 | 23.8523 | 13.8937 | 8.8769 | 6.2786
2400 | 1999.2 | 814.8999 | 345.9323 | 210.9306 | 141.3235 | 92.2584 | 54.0271 | 34.9745 | 24.2565 | 14.1292 | 9.0273 | 6.385
2440 | 2032.52 | 828.4815 | 351.6978 | 214.4461 | 143.6788 | 93.796 | 54.9276 | 35.5574 | 24.6608 | 14.3647 | 9.1778 | 6.4914
2480 | 2065.84 | 842.0632 | 357.4633 | 217.9616 | 146.0342 | 95.3337 | 55.828 | 36.1403 | 25.0651 | 14.6002 | 9.3282 | 6.5979
2520 | 2099.16 | 855.6449 | 363.2289 | 221.4771 | 148.3896 | 96.8713 | 56.7285 | 36.7232 | 25.4694 | 14.8356 | 9.4787 | 6.7043
2560 | 2132.48 | 869.2265 | 368.9944 | 224.9926 | 150.745 | 98.4089 | 57.6289 | 37.3061 | 25.8737 | 15.0711 | 9.6291 | 6.8107
2600 | 2165.8 | 882.8082 | 374.76 | 228.5082 | 153.1004 | 99.9466 | 58.5294 | 37.889 | 26.2779 | 15.3066 | 9.7796 | 6.9171
2640 | 2199.12 | 896.3899 | 380.5255 | 232.0237 | 155.4558 | 101.4842 | 59.4299 | 38.4719 | 26.6822 | 15.5421 | 9.93 | 7.0235
2680 | 2232.44 | 909.9715 | 386.291 | 235.5392 | 157.8112 | 103.0219 | 60.3303 | 39.0548 | 27.0865 | 15.7776 | 10.0805 | 7.1299
2720 | 2265.76 | 923.5532 | 392.0566 | 239.0547 | 160.1666 | 104.5595 | 61.2308 | 39.6377 | 27.4908 | 16.0131 | 10.231 | 7.2364
2760 | 2299.08 | 937.1349 | 397.8221 | 242.5702 | 162.522 | 106.0971 | 62.1312 | 40.2206 | 27.895 | 16.2486 | 10.3814 | 7.3428
2800 | 2332.4 | 950.7165 | 403.5877 | 246.0857 | 164.8774 | 107.6348 | 63.0317 | 40.8035 | 28.2993 | 16.4841 | 10.5319 | 7.4492
2840 | 2365.72 | 964.2982 | 409.3532 | 249.6012 | 167.2328 | 109.1724 | 63.9321 | 41.3864 | 28.7036 | 16.7195 | 10.6823 | 7.5556
2880 | 2399.04 | 977.8798 | 415.1187 | 253.1167 | 169.5881 | 110.71 | 64.8326 | 41.9694 | 29.1079 | 16.955 | 10.8328 | 7.662
2920 | 2432.36 | 991.4615 | 420.8843 | 256.6322 | 171.9435 | 112.2477 | 65.733 | 42.5523 | 29.5121 | 17.1905 | 10.9832 | 7.7684
2960 | 2465.68 | 1005.0432 | 426.6498 | 260.1477 | 174.2989 | 113.7853 | 66.6335 | 43.1352 | 29.9164 | 17.426 | 11.1337 | 7.8749
3000 | 2499 | 1018.6248 | 432.4153 | 263.6633 | 176.6543 | 115.323 | 67.5339 | 43.7181 | 30.3207 | 17.6615 | 11.2841 | 7.9813
3040 | 2532.32 | 1032.2065 | 438.1809 | 267.1788 | 179.0097 | 116.8606 | 68.4344 | 44.301 | 30.725 | 17.897 | 11.4346 | 8.0877
3080 | 2565.64 | 1045.7882 | 443.9464 | 270.6943 | 181.3651 | 118.3982 | 69.3348 | 44.8839 | 31.1292 | 18.1325 | 11.5851 | 8.1941
3120 | 2598.96 | 1059.3698 | 449.712 | 274.2098 | 183.7205 | 119.9359 | 70.2353 | 45.4668 | 31.5335 | 18.3679 | 11.7355 | 8.3005
3160 | 2632.28 | 1072.9515 | 455.4775 | 277.7253 | 186.0759 | 121.4735 | 71.1357 | 46.0497 | 31.9378 | 18.6034 | 11.886 | 8.4069
3200 | 2665.6 | 1086.5332 | 461.243 | 281.2408 | 188.4313 | 123.0112 | 72.0362 | 46.6326 | 32.3421 | 18.8389 | 12.0364 | 8.5134
3240 | 2698.92 | 1100.1148 | 467.0086 | 284.7563 | 190.7867 | 124.5488 | 72.9366 | 47.2155 | 32.7463 | 19.0744 | 12.1869 | 8.6198
3280 | 2732.24 | 1113.6965 | 472.7741 | 288.2718 | 193.1421 | 126.0864 | 73.8371 | 47.7984 | 33.1506 | 19.3099 | 12.3373 | 8.7262
3320 | 2765.56 | 1127.2782 | 478.5396 | 291.7873 | 195.4974 | 127.6241 | 74.7375 | 48.3813 | 33.5549 | 19.5454 | 12.4878 | 8.8326
3360 | 2798.88 | 1140.8598 | 484.3052 | 295.3028 | 197.8528 | 129.1617 | 75.638 | 48.9643 | 33.9592 | 19.7809 | 12.6382 | 8.939
3400 | 2832.2 | 1154.4415 | 490.0707 | 298.8184 | 200.2082 | 130.6994 | 76.5384 | 49.5472 | 34.3634 | 20.0164 | 12.7887 | 9.0455
3440 | 2865.52 | 1168.0231 | 495.8363 | 302.3339 | 202.5636 | 132.237 | 77.4389 | 50.1301 | 34.7677 | 20.2518 | 12.9392 | 9.1519
3480 | 2898.84 | 1181.6048 | 501.6018 | 305.8494 | 204.919 | 133.7746 | 78.3393 | 50.713 | 35.172 | 20.4873 | 13.0896 | 9.2583
3520 | 2932.16 | 1195.1865 | 507.3673 | 309.3649 | 207.2744 | 135.3123 | 79.2398 | 51.2959 | 35.5763 | 20.7228 | 13.2401 | 9.3647
3560 | 2965.48 | 1208.7681 | 513.1329 | 312.8804 | 209.6298 | 136.8499 | 80.1403 | 51.8788 | 35.9805 | 20.9583 | 13.3905 | 9.4711
3600 | 2998.8 | 1222.3498 | 518.8984 | 316.3959 | 211.9852 | 138.3876 | 81.0407 | 52.4617 | 36.3848 | 21.1938 | 13.541 | 9.5775
3640 | 3032.12 | 1235.9315 | 524.6639 | 319.9114 | 214.3406 | 139.9252 | 81.9412 | 53.0446 | 36.7891 | 21.4293 | 13.6914 | 9.684
3680 | 3065.44 | 1249.5131 | 530.4295 | 323.4269 | 216.696 | 141.4628 | 82.8416 | 53.6275 | 37.1934 | 21.6648 | 13.8419 | 9.7904
3720 | 3098.76 | 1263.0948 | 536.195 | 326.9424 | 219.0514 | 143.0005 | 83.7421 | 54.2104 | 37.5976 | 21.9002 | 13.9923 | 9.8968
3760 | 3132.08 | 1276.6765 | 541.9606 | 330.4579 | 221.4067 | 144.5381 | 84.6425 | 54.7933 | 38.0019 | 22.1357 | 14.1428 | 10.0032
3800 | 3165.4 | 1290.2581 | 547.7261 | 333.9735 | 223.7621 | 146.0758 | 85.543 | 55.3762 | 38.4062 | 22.3712 | 14.2932 | 10.1096
3840 | 3198.72 | 1303.8398 | 553.4916 | 337.489 | 226.1175 | 147.6134 | 86.4434 | 55.9591 | 38.8105 | 22.6067 | 14.4437 | 10.216
3880 | 3232.04 | 1317.4215 | 559.2572 | 341.0045 | 228.4729 | 149.151 | 87.3439 | 56.5421 | 39.2148 | 22.8422 | 14.5942 | 10.3225
3920 | 3265.36 | 1331.0031 | 565.0227 | 344.52 | 230.8283 | 150.6887 | 88.2443 | 57.125 | 39.619 | 23.0777 | 14.7446 | 10.4289
3960 | 3298.68 | 1344.5848 | 570.7882 | 348.0355 | 233.1837 | 152.2263 | 89.1448 | 57.7079 | 40.0233 | 23.3132 | 14.8951 | 10.5353
4000 | 3332 | 1358.1664 | 576.5538 | 351.551 | 235.5391 | 153.764 | 90.0452 | 58.2908 | 40.4276 | 23.5486 | 15.0455 | 10.6417
4040 | 3365.32 | 1371.7481 | 582.3193 | 355.0665 | 237.8945 | 155.3016 | 90.9457 | 58.8737 | 40.8319 | 23.7841 | 15.196 | 10.7481
4080 | 3398.64 | 1385.3298 | 588.0849 | 358.582 | 240.2499 | 156.8392 | 91.8461 | 59.4566 | 41.2361 | 24.0196 | 15.3464 | 10.8545
4120 | 3431.96 | 1398.9114 | 593.8504 | 362.0975 | 242.6053 | 158.3769 | 92.7466 | 60.0395 | 41.6404 | 24.2551 | 15.4969 | 10.961
4160 | 3465.28 | 1412.4931 | 599.6159 | 365.613 | 244.9607 | 159.9145 | 93.647 | 60.6224 | 42.0447 | 24.4906 | 15.6473 | 11.0674
4200 | 3498.6 | 1426.0748 | 605.3815 | 369.1286 | 247.316 | 161.4522 | 94.5475 | 61.2053 | 42.449 | 24.7261 | 15.7978 | 11.1738
4240 | 3531.92 | 1439.6564 | 611.147 | 372.6441 | 249.6714 | 162.9898 | 95.4479 | 61.7882 | 42.8532 | 24.9616 | 15.9483 | 11.2802
4280 | 3565.24 | 1453.2381 | 616.9126 | 376.1596 | 252.0268 | 164.5274 | 96.3484 | 62.3711 | 43.2575 | 25.1971 | 16.0987 | 11.3866
4320 | 3598.56 | 1466.8198 | 622.6781 | 379.6751 | 254.3822 | 166.0651 | 97.2488 | 62.954 | 43.6618 | 25.4325 | 16.2492 | 11.493
4360 | 3631.88 | 1480.4014 | 628.4436 | 383.1906 | 256.7376 | 167.6027 | 98.1493 | 63.5369 | 44.0661 | 25.668 | 16.3996 | 11.5995
4400 | 3665.2 | 1493.9831 | 634.2092 | 386.7061 | 259.093 | 169.1404 | 99.0498 | 64.1199 | 44.4703 | 25.9035 | 16.5501 | 11.7059
4440 | 3698.52 | 1507.5648 | 639.9747 | 390.2216 | 261.4484 | 170.678 | 99.9502 | 64.7028 | 44.8746 | 26.139 | 16.7005 | 11.8123